XS型

单级双吸立式离心泵

Type SL Single-stage Double-suction Vertical

Centrifugal Pump

安装使用说明书

# Instrutions on Installtion and Operation

长沙福斯水泵泵业有限公司

Fuchs Changsha Pump pump industry limited company

产品概述

一、概述:

XS型泵系新一代高性能单级双吸水平中开式离心泵，主要适用于自来水厂空调循环用水，供热管网系统、建筑供水、灌溉、排水泵站、电厂、工业供水系统、消防系统、船舶工业、矿山给排水等领域。

参数范围： 流量Q   22～11600m3/h      扬程H  7～200m

型号说明：

如：XS250-450A

XS------新型中开泵

250-----水泵出口直径

450-----叶轮直径

A-------表示叶轮外径第一次变化，A、B、C……依次类推

XS型泵的主要技术参数：

泵出口直径DN：					80～800mm

流量        Q：					22～11600m3/h

扬程 		 H：					7～200m

工作温度	 T：					-20℃～105℃

固体颗粒:	    					≤80mg/L

工作许用压力：					≤2.5MPa

## GENERAL

Type XS pumps are new type of single stage double suction centrifugal split pumps with high performance. They are widely used in delivering liquids to the water plant, circulation water system of air-conditioner pipe net system of supplying heated water, construction, drainage pumping station, power-station, industrial water supply system ship industry, mine and etc.

THE TECHNICAL PARMETER OF TYPE XS PUMPS:

Pump outlet diameter DN:			80～800mm

Capacity              Q:			22～11600m3/h

Head                  H:			7～200m

Temperature           T:			-20℃～105℃

Solid parameter :     			≤80mg/L

Permissible pressure :  			≤2.5MPa

技术优势：

1、水泵两端支承间距短，泵运行稳定，振动噪声小，并呆适当升速运行，使水泵适应范围更广。

2、同一转子可反向运行，降低了水锤引起水泵损坏的风险。

3、独特的高温型设计，水泵采用中间支撑，加厚泵体，密封冷却、轴承稀油润滑等，使水泵可应用于高达200℃运行场合，特别适应于供热管网使用要求。

4、密封可采用机械密封或填料密封。

5、水泵外型应用工业化设计，线条清晰，符合现代审美观。

成本优势：

1、选用优异的水力模型，使泵的效率比同类型泵高2-3%，大大降低了泵的运行成本。

2、真空高度提高1-3米，从而降低低土建投资，延长了使用寿命。

3、选用进口轴承，零件材料可根据用户要求选用，使泵能适应各种现场运行条件，大大降低了维修成本。

维修优势：

1、集装式机械密封，更换机械密封成为轻松简单的工作。

2、应用弹性预应力装配，转子部件装拆简单迅速。

3、装配时不需调整各种间隙。

TECHNICAL ADVANTAGE:

1. Type SL pumps work stably with less noise and vibration and can work at a lifting speed due to short support at both sides, thus they can widely used.

2. The same rotor of Type SL pumps can be operated at reverse direction to avoid damage to the pumps by water hammer.

3. Unique design of type SL pumps working at high temperature using middle support to fasten the pump casing and using cooling seals oil lubrication bearing then pump suitable for working at 200℃ especially for suppling heated water to pipe net system.

4. Type SL with mechanical seals or packing seals.

5. Type SL pumps look beautiful with visible lines adopting industrially designing.

COST ADVANTAGE:

1. The efficiency of SL pumps are 2%～3% higher than the same type pumps due to adopting advanced hydraulic model and thus minimum the operating costs.

2. The NPSH of type SL pumps are 1～3 meters lower than the same type split pumps due to using advanced hydraulic model and advanced manufacturing technique and thus minimize the foundation costs and extendling the using life.

3. Type SL pumps are suitable for any site working condition due to using SKF or NSK bearing and other parts chosen by the customers and thus minimize the maintenance costs.

MAINTENANCE ADVANTAGE:

1. It is very easy and simple to replace the mechanical seal due to usine container type mechanical seal.

2. It is rapid and easy to assembly and dismount the rotor parts due to using elastic ripess assembling.

3. It is unnecessary to make adjustment when assembling.

主要零件材料表（Main part material list）

| 零件名称 part name | 材料名称 material name | 代号 GB code |
| --- | --- | --- |
| 泵壳 Pump casing | 灰铸铁 球墨铸铁 铸钢 | HT250 QT400-18 ZG230-450 |
| 叶轮 Impeller | 青铜 灰铸铁 硅黄铜 不锈钢 | ZCuSn10Pb1 HT250 ZCuZn6Si4 ZG0Cr18Ni12Mo2Ti |
| 轴 Shaft | 不锈钢 碳钢 | 2Cr12 45 |
| 泵体密封环 ring | 青铜 灰铸铁 硅黄铜 不锈钢 | ZCuSn10Pb1 HT250 ZCuZn6Si4 ZG0Cr18Ni12Mo2Ti |

三、结构图 Construction

XS型卧式泵结构图(Construction of type XS pump):

1、泵体           2、叶轮         3、泵盖            4、水冲洗管部件

casing          impeller          casing cover        water flushing pipe parts

5、密封环         6、管堵         7、O形密封圈      8、密封体

ring           pipe nut          “O” sealing ring     sealing support

9、密封压盖或填料压盖             10、挡水圈         11、轴承压盖

sealing gland or packing gland        water deflector       bearing gland

12、轴承体        13、轴           14、骨架油封      15、弹性挡圈

bearing support     shaft            oil seal            elastic deflector

16、轴承挡圈      17、轴套        18、机械密封或填料密封       19、轴承套

bearing deflector   shaft sleeve      mechanical seal or packing seal   bearing sleeve

20、轴承          21轴承垫圈      22、碟形弹簧       23、锁紧螺母

bearing           bearing ring       butterfly spring       lock-nut

四、XS型谱图（selection chart of XS pump）

性能参数（Performance Data）

| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 80-210 |  | 22.0 | 6.1 | 17.0 | 1480 | 5.5 | 82 | 1.6 |
|  |  | 83.5 | 23.2 | 13.8 |  |  |  |  |
|  |  | 121.0 | 33.6 | 10.0 |  |  |  |  |
|  | A | 20.0 | 5.6 | 14.8 |  | 4 | 81 |  |
|  |  | 77.2 | 21.4 | 11.8 |  |  |  |  |
|  |  | 108.0 | 30.0 | 8.7 |  |  |  |  |
|  | B | 17.5 | 4.86 | 12.4 |  | 3 | 80.5 |  |
|  |  | 70.4 | 19.6 | 9.8 |  |  |  |  |
|  |  | 96.0 | 26.6 | 7.7 |  |  |  |  |
|  | C | 16.0 | 4.4 | 10.6 |  | 3 | 78 |  |
|  |  | 64.4 | 17.9 | 8.2 |  |  |  |  |
|  |  | 83.0 | 23.0 | 6.8 |  |  |  |  |
|  |  | 60.0 | 16.7 | 64.5 | 2950 | 37 | 82 | 4.5 |
|  |  | 164.5 | 45.7 | 55.0 |  |  |  |  |
|  |  | 240.0 | 66.7 | 40.0 |  |  |  |  |
|  | A | 59.0 | 16.3 | 58.0 |  | 30 | 81 |  |
|  |  | 152.9 | 42.5 | 47.5 |  |  |  |  |
|  |  | 219.0 | 60.8 | 34.0 |  |  |  |  |
|  | B | 55.0 | 15.3 | 49.0 |  | 30 | 80.5 |  |
|  |  | 138.5 | 38.5 | 39.0 |  |  |  |  |
|  |  | 199.0 | 55.3 | 30.0 |  |  |  |  |
|  | C | 52.0 | 14.4 | 42.0 |  | 22 | 77.8 |  |
|  |  | 128.4 | 35.7 | 33.5 |  |  |  |  |
|  |  | 170.0 | 47.0 | 27.5 |  |  |  |  |
| 80-270 |  | 26.0 | 7.2 | 24.5 | 1480 | 11 | 78.5 | 2.3 |
|  |  | 104.5 | 29.0 | 22.5 |  |  |  |  |
|  |  | 138.0 | 38.3 | 18.0 |  |  |  |  |
|  | A | 25.0 | 6.9 | 22.0 |  | 11 | 78 |  |
|  |  | 96 | 26.7 | 19.0 |  |  |  |  |
|  |  | 129.0 | 35.8 | 16.0 |  |  |  |  |
|  | B | 22.0 | 6.1 | 19.5 |  | 7.5 | 76 |  |
|  |  | 88.1 | 24.5 | 16.0 |  |  |  |  |
|  |  | 116.0 | 32.2 | 13.0 |  |  |  |  |
|  | C | 21.0 | 5.8 | 16.8 |  | 5.5 | 75 |  |
|  |  | 79.4 | 22.0 | 13.0 |  |  |  |  |
|  |  | 105.0 | 29.0 | 10.5 |  |  |  |  |
|  |  | 80.0 | 22.0 | 107.0 | 2950 | 75 | 78.5 | 6.3 |
|  |  | 208.0 | 57.8 | 90.0 |  |  |  |  |
|  |  | 280.0 | 77.8 | 77.5 |  |  |  |  |
|  | A | 78.0 | 21.7 | 92.5 |  | 75 | 77.5 |  |
|  |  | 192.4 | 53.4 | 77.0 |  |  |  |  |
|  |  | 235.0 | 65.3 | 68.0 |  |  |  |  |
|  | B | 75.0 | 20.8 | 77.5 |  | 55 | 76 |  |
|  |  | 174.7 | 48.5 | 63.5 |  |  |  |  |
|  |  | 220.0 | 61.1 | 55.0 |  |  |  |  |
|  | C | 74.0 | 20.5 | 64.0 |  | 37 | 75 |  |
|  |  | 155.0 | 43.0 | 50.0 |  |  |  |  |
|  |  | 200.0 | 55.6 | 45.0 |  |  |  |  |
| 80-370 |  | 29.0 | 8.1 | 43.5 | 1480 | 22 | 71.5 | 2.3 |
|  |  | 114.4 | 31.8 | 38.8 |  |  |  |  |
|  |  | 15.0 | 41.7 | 29.3 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 80-370 | A | 26.0 | 7.2 | 37.5 | 1480 | 15 | 70.5 | 2.3 |
|  |  | 105.5 | 29.3 | 33.0 |  |  |  |  |
|  |  | 133.0 | 26.9 | 25.0 |  |  |  |  |
|  | B | 22.0 | 6.1 | 32.0 |  | 15 | 70 |  |
|  |  | 96.3 | 26.8 | 27.5 |  |  |  |  |
|  |  | 117.0 | 32.5 | 22.0 |  |  |  |  |
|  | C | 20.0 | 5.6 | 26.0 |  | 11 | 67.5 |  |
|  |  | 87.1 | 24.2 | 22.5 |  |  |  |  |
|  |  | 102.0 | 28.3 | 17.9 |  |  |  |  |
| 100-250 |  | 38.0 | 10.6 | 23.5 | 1480 | 11 | 82.5 | 2.4 |
|  |  | 145.0 | 40.3 | 18.8 |  |  |  |  |
|  |  | 212.0 | 58.9 | 13.1 |  |  |  |  |
|  | A | 37.0 | 10.3 | 20.1 |  | 11 | 81 |  |
|  |  | 132.9 | 36.9 | 15.8 |  |  |  |  |
|  |  | 192.0 | 53.0 | 11.5 |  |  |  |  |
|  | B | 36.0 | 10.0 | 17.0 |  | 7.5 | 79 |  |
|  |  | 122.9 | 34.1 | 13.5 |  |  |  |  |
|  |  | 173.0 | 48.1 | 10.2 |  |  |  |  |
|  | C | 34.0 | 9.4 | 14.5 |  | 5.5 | 77.5 |  |
|  |  | 115.9 | 32.2 | 11.0 |  |  |  |  |
|  |  | 154.0 | 42.8 | 8.9 |  |  |  |  |
|  |  | 148.5 | 41.3 | 90.0 | 2950 | 90 | 82.5 | 7.1 |
|  |  | 289.0 | 80.3 | 75.0 |  |  |  |  |
|  |  | 375.0 | 104.2 | 82.0 |  |  |  |  |
|  | A | 120.8 | 33.6 | 8.5 |  | 75 | 80.5 |  |
|  |  | 264.9 | 73.6 | 63.0 |  |  |  |  |
|  |  | 340.0 | 94.0 | 52.9 |  |  |  |  |
|  | B | 70.0 | 19.4 | 67.5 |  | 55 | 79 |  |
|  |  | 240.5 | 66.8 | 52.0 |  |  |  |  |
|  |  | 325.0 | 90.3 | 43.5 |  |  |  |  |
|  | C | 60.0 | 16.7 | 57.2 |  | 45 | 78 |  |
|  |  | 223.4 | 62.0 | 44.8 |  |  |  |  |
|  |  | 295.0 | 81.9 | 36.0 |  |  |  |  |
| 100-310 |  | 47.0 | 13.1 | 38.1 | 1480 | 22 | 80 | 2.6 |
|  |  | 185.5 | 51.5 | 31.2 |  |  |  |  |
|  |  | 225.0 | 62.5 | 26.0 |  |  |  |  |
|  | A | 42.0 | 11.7 | 33.2 |  | 18.5 | 79.6 |  |
|  |  | 172.6 | 47.9 | 27.0 |  |  |  |  |
|  |  | 204.0 | 56.7 | 22.5 |  |  |  |  |
|  | B | 38.0 | 10.6 | 27.9 |  | 15 | 79.3 |  |
|  |  | 157.5 | 43.8 | 22.5 |  |  |  |  |
|  |  | 184.0 | 51.1 | 18.5 |  |  |  |  |
|  | C | 37.0 | 10.3 | 23.2 |  | 11 | 79 |  |
|  |  | 142.8 | 39.7 | 18.5 |  |  |  |  |
|  |  | 165.0 | 45.8 | 16.0 |  |  |  |  |
|  |  | 185.0 | 51.4 | 148.0 | 2950 | 200 | 80 | 11 |
|  |  | 368.0 | 102.2 | 123.0 |  |  |  |  |
|  |  | 450.0 | 125.0 | 102.0 |  |  |  |  |
|  | A | 140.0 | 38.9 | 130.0 |  | 132 | 79.6 |  |
|  |  | 341.6 | 94.9 | 106.0 |  |  |  |  |
|  |  | 410.0 | 113.9 | 89.5 |  |  |  |  |
|  | B | 100.0 | 27.7 | 110.0 |  | 110 | 79.3 |  |
|  |  | 314.8 | 87.4 | 90.0 |  |  |  |  |
|  |  | 370.0 | 102.8 | 77.3 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 100-310 | C | 119.0 | 33.1 | 93.5 | 2950 | 90 | 79 | 11 |
|  |  | 245.4 | 68.2 | 74.0 |  |  |  |  |
|  |  | 325.0 | 90.3 | 64.0 |  |  |  |  |
| 100-375 |  | 70.0 | 19.4 | 693.0 | 1480 | 45 | 73 | 2.5 |
|  |  | 185.5 | 51.5 | 52.0 |  |  |  |  |
|  |  | 241.5 | 67.0 | 39.0 |  |  |  |  |
|  | A | 65.0 | 18.1 | 53.0 |  | 30 | 72 |  |
|  |  | 170.6 | 47.4 | 44.0 |  |  |  |  |
|  |  | 213.0 | 59.2 | 34.0 |  |  |  |  |
|  | B | 62.0 | 17.2 | 46.0 |  | 30 | 71 |  |
|  |  | 158.6 | 44.0 | 38.0 |  |  |  |  |
|  |  | 190.0 | 52.8 | 31.2 |  |  |  |  |
|  | C | 58.0 | 16.1 | 35.5 |  | 18.5 | 69 |  |
|  |  | 141.6 | 39.3 | 30.3 |  |  |  |  |
|  |  | 178.0 | 49.4 | 22.5 |  |  |  |  |
| 125-230 |  | 100.0 | 27.8 | 20.2 | 1480 | 18.5 | 85.5 | 1.8 |
|  |  | 274.6 | 76.3 | 14.8 |  |  |  |  |
|  |  | 370.6 | 102.8 | 9.1 |  |  |  |  |
|  | A | 92.0 | 25.6 | 18.3 |  | 15 | 84.5 |  |
|  |  | 259.3 | 72.0 | 13.2 |  |  |  |  |
|  |  | 332.0 | 92.2 | 8.3 |  |  |  |  |
|  | B | 82.0 | 22.8 | 15.9 |  | 15 | 82.5 |  |
|  |  | 232.4 | 64.5 | 10.6 |  |  |  |  |
|  |  | 285.0 | 79.2 | 7.6 |  |  |  |  |
|  | C | 78.0 | 21.7 | 13.2 |  | 11 | 77.5 |  |
|  |  | 210.5 | 58.5 | 8.7 |  |  |  |  |
|  |  | 240.0 | 66.7 | 6.8 |  |  |  |  |
|  |  | 139.5 | 38.7 | 83.5 | 2950 | 132 | 85.5 | 6.8 |
|  |  | 533.5 | 148.2 | 60.0 |  |  |  |  |
|  |  | 715.0 | 198.6 | 40.0 |  |  |  |  |
|  | A | 124.0 | 34.4 | 73.0 |  | 110 | 84 |  |
|  |  | 496.7 | 138.0 | 52.0 |  |  |  |  |
|  |  | 650.0 | 180.6 | 36.0 |  |  |  |  |
|  | B | 119.0 | 33.1 | 63.5 |  | 75 | 82 |  |
|  |  | 454.3 | 126.2 | 43.5 |  |  |  |  |
|  |  | 550.0 | 152.8 | 32.0 |  |  |  |  |
|  | C | 103.0 | 28.6 | 63.0 |  | 75 | 77 |  |
|  |  | 411.6 | 114.3 | 34.0 |  |  |  |  |
|  |  | 460.0 | 127.8 | 30.0 |  |  |  |  |
| 125-290 |  | 100.0 | 27.8 | 32.5 | 1480 | 30 | 84 | 1.9 |
|  |  | 270.0 | 75.0 | 27.0 |  |  |  |  |
|  |  | 375.0 | 104.2 | 21.0 |  |  |  |  |
|  | A | 80.3 | 22.3 | 27.5 |  | 22 | 82 |  |
|  |  | 243.7 | 67.7 | 22.0 |  |  |  |  |
|  |  | 348.0 | 96.7 | 15.5 |  |  |  |  |
|  | B | 75.0 | 20.8 | 23.5 |  | 18.5 | 80 |  |
|  |  | 220.5 | 61.2 | 18.0 |  |  |  |  |
|  |  | 310.0 | 86.1 | 12.5 |  |  |  |  |
|  | C | 60.5 | 16.8 | 19.0 |  | 15 | 78 |  |
|  |  | 195.8 | 54.4 | 14.2 |  |  |  |  |
|  |  | 270.0 | 75.0 | 10.5 |  |  |  |  |
|  |  | 380.0 | 105.6 | 120.0 |  | 200 | 84 | 7.6 |
|  |  | 535.5 | 148.8 | 108.0 |  |  |  |  |
|  |  | 640.0 | 177.8 | 92.6 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 125-290 | A | 285.0 | 79.2 | 103.5 | 2950 | 160 | 82 | 7.6 |
|  |  | 483.0 | 134.3 | 88.0 |  |  |  |  |
|  |  | 630.0 | 175.0 | 77.8 |  |  |  |  |
|  | B | 190.0 | 52.3 | 92.0 |  | 132 | 80 |  |
|  |  | 437.2 | 121.5 | 72.0 |  |  |  |  |
|  |  | 600.0 | 166.7 | 60.0 |  |  |  |  |
|  | C | 90.2 | 25.1 | 80.0 |  | 110 | 78 |  |
|  |  | 389.0 | 108.1 | 57.0 |  |  |  |  |
|  |  | 500.0 | 138.9 | 43.5 |  |  |  |  |
| 125-365 |  | 125.0 | 34.78 | 53.1 | 1480 | 75 | 80 | 2.1 |
|  |  | 310.5 | 86.3 | 47.0 |  |  |  |  |
|  |  | 435.0 | 120.8 | 37.5 |  |  |  |  |
|  | A | 104.0 | 28.9 | 45.0 |  | 45 | 79 |  |
|  |  | 282.8 | 78.6 | 39.0 |  |  |  |  |
|  |  | 395.0 | 109.7 | 31.8 |  |  |  |  |
|  | B | 93.0 | 25.8 | 36.9 |  | 37 | 78 |  |
|  |  | 254.2 | 70.6 | 31.5 |  |  |  |  |
|  |  | 350.2 | 97.2 | 25.0 |  |  |  |  |
|  | C | 85.5 | 23.7 | 27.9 |  | 30 | 76 |  |
|  |  | 221.9 | 61.6 | 24.0 |  |  |  |  |
|  |  | 295.2 | 109.8 | 18.8 |  |  |  |  |
| 125-500 |  | 109.2 | 30.3 | 86.0 | 1480 | 110 | 80 | 2.3 |
|  |  | 328.5 | 91.3 | 76.0 |  |  |  |  |
|  |  | 380.4 | 105.7 | 71.0 |  |  |  |  |
|  | A | 100.0 | 27.8 | 74.9 |  | 90 | 78.5 |  |
|  |  | 307.3 | 85.4 | 66.5 |  |  |  |  |
|  |  | 350.9 | 97.4 | 55.0 |  |  |  |  |
|  | B | 80.4 | 22.3 | 64.7 |  | 75 | 77 |  |
|  |  | 282.0 | 78.3 | 56.0 |  |  |  |  |
|  |  | 300.4 | 83.4 | 51.3 |  |  |  |  |
|  | C | 60.0 | 16.6 | 54.6 |  | 45 | 76 |  |
|  |  | 250.4 | 69.6 | 44.2 |  |  |  |  |
|  |  | 270.4 | 75.1 | 40.8 |  |  |  |  |
| 150-290 |  | 160.0 | 44.4 | 27.5 | 1480 | 37 | 87 | 2.4 |
|  |  | 443.5 | 123.2 | 21.0 |  |  |  |  |
|  |  | 609.0 | 169.2 | 14.2 |  |  |  |  |
|  | A | 150.5 | 41.8 | 25.0 |  | 30 | 86 |  |
|  |  | 410.6 | 114.0 | 18.0 |  |  |  |  |
|  |  | 550.0 | 152.8 | 12.5 |  |  |  |  |
|  | B | 130.0 | 36.1 | 22.5 |  | 22 | 84 |  |
|  |  | 367.0 | 101.9 | 15.0 |  |  |  |  |
|  |  | 480.0 | 133.3 | 11.7 |  |  |  |  |
|  | C | 123.0 | 34.1 | 17.4 |  | 18.5 | 77 |  |
|  |  | 338.2 | 93.9 | 11.5 |  |  |  |  |
|  |  | 395.0 | 109.7 | 10.0 |  |  |  |  |
| 150-360 |  | 180.0 | 50.0 | 45.8 | 1480 | 75 | 85 | 2.5 |
|  |  | 447.0 | 124.3 | 38.0 |  |  |  |  |
|  |  | 592.0 | 164.4 | 31.2 |  |  |  |  |
|  | A | 175.0 | 48.6 | 38.6 |  | 55 | 83 |  |
|  |  | 404.2 | 112.3 | 31.0 |  |  |  |  |
|  |  | 580.0 | 161.1 | 22.4 |  |  |  |  |
|  | B | 162.0 | 45.0 | 33.1 |  | 37 | 81 |  |
|  |  | 363.0 | 100.8 | 25.0 |  |  |  |  |
|  |  | 495.0 | 137.5 | 18.1 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 150-360 | C | 150.0 | 41.7 | 27.8 | 1480 | 30 | 78 | 2.5 |
|  |  | 324.7 | 90.2 | 20.0 |  |  |  |  |
|  |  | 421.0 | 116.9 | 14.9 |  |  |  |  |
| 150-450 |  | 200.0 | 55.6 | 76.1 | 1480 | 132 | 82 | 3.0 |
|  |  | 515.5 | 143.2 | 66.0 |  |  |  |  |
|  |  | 640.0 | 177.8 | 57.1 |  |  |  |  |
|  | A | 190.0 | 52.8 | 64.0 |  | 110 | 81 |  |
|  |  | 468.4 | 130.1 | 54.5 |  |  |  |  |
|  |  | 600.0 | 166.7 | 45.0 |  |  |  |  |
|  | B | 180.0 | 50.0 | 52.3 |  | 75 | 80 |  |
|  |  | 418.5 | 116.3 | 43.5 |  |  |  |  |
|  |  | 540.0 | 150.0 | 35.0 |  |  |  |  |
|  | C | 175.0 | 48.6 | 42.1 |  | 55 | 78.5 |  |
|  |  | 375.4 | 104.3 | 35.0 |  |  |  |  |
|  |  | 468.0 | 130.0 | 27.8 |  |  |  |  |
| 150-605 |  | 200.0 | 55.6 | 121.0 | 1480 | 250 | 80 | 3.7 |
|  |  | 584.0 | 162.2 | 105.0 |  |  |  |  |
|  |  | 730.0 | 202.8 | 92.1 |  |  |  |  |
|  | A | 180.0 | 50.0 | 105.0 |  | 200 | 79 |  |
|  |  | 536.2 | 148.9 | 88.5 |  |  |  |  |
|  |  | 660.0 | 183.3 | 80.0 |  |  |  |  |
|  | B | 169.0 | 46.9 | 90.8 |  | 160 | 78 |  |
|  |  | 493.6 | 137.1 | 75.0 |  |  |  |  |
|  |  | 620.0 | 172.2 | 68.0 |  |  |  |  |
|  | C | 150.0 | 41.7 | 77.2 |  | 132 | 77 |  |
|  |  | 450.0 | 125.0 | 61.5 |  |  |  |  |
|  |  | 530.0 | 147.2 | 55.9 |  |  |  |  |
| 200-320 |  | 250.0 | 69.4 | 40.0 | 1480 | 75 | 87.5 | 3.3 |
|  |  | 695.5 | 193.2 | 30.0 |  |  |  |  |
|  |  | 940.0 | 261.1 | 20.2 |  |  |  |  |
|  | A | 240.0 | 66.7 | 35.0 |  | 75 | 86.5 |  |
|  |  | 641.2 | 178.1 | 25.5 |  |  |  |  |
|  |  | 845.0 | 234.7 | 17.5 |  |  |  |  |
|  | B | 230.0 | 63.9 | 30.8 |  | 55 | 85 |  |
|  |  | 585.0 | 162.8 | 21.3 |  |  |  |  |
|  |  | 750.0 | 208.3 | 16.0 |  |  |  |  |
|  | C | 220.0 | 61.1 | 25.0 |  | 37 | 79 |  |
|  |  | 530.0 | 147.2 | 17.0 |  |  |  |  |
|  |  | 610.0 | 169.4 | 15.1 |  |  |  |  |
| 200-420 |  | 265.0 | 73.6 | 62.8 | 1480 | 132 | 86.5 | 2.4 |
|  |  | 710.0 | 197.2 | 52.0 |  |  |  |  |
|  |  | 990.0 | 275.0 | 40.0 |  |  |  |  |
|  | A | 249.0 | 69.1 | 64.0 |  | 110 | 84.5 |  |
|  |  | 641.9 | 178.3 | 42.5 |  |  |  |  |
|  |  | 895.0 | 248.6 | 30.9 |  |  |  |  |
|  | B | 238.0 | 66.1 | 46.0 |  | 90 | 83 |  |
|  |  | 586.6 | 163.0 | 35.5 |  |  |  |  |
|  |  | 780.0 | 216.7 | 25.0 |  |  |  |  |
|  | C | 220.0 | 61.1 | 28.5 |  | 75 | 81 |  |
|  |  | 525.6 | 146.0 | 28.5 |  |  |  |  |
|  |  | 660.0 | 166.7 | 21.0 |  |  |  |  |
| 200-520 |  | 475.0 | 131.9 | 102.0 | 1480 | 280 | 83 | 3.5 |
|  |  | 818.0 | 227.2 | 91.0 |  |  |  |  |
|  |  | 1080 | 300.0 | 77.5 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 200-520 | A | 460.0 | 127.8 | 86.0 | 1480 | 250 | 82 | 3.5 |
|  |  | 750.0 | 208.3 | 76.5 |  |  |  |  |
|  |  | 965.0 | 268.1 | 66.2 |  |  |  |  |
|  | B | 440.0 | 122.2 | 71.0 |  | 200 | 80 |  |
|  |  | 687.9 | 191.1 | 62.5 |  |  |  |  |
|  |  | 905.0 | 251.4 | 52.1 |  |  |  |  |
|  | C | 420.0 | 116.7 | 55.0 |  | 132 | 78.5 |  |
|  |  | 630.0 | 175.0 | 47.5 |  |  |  |  |
|  |  | 795.0 | 220.8 | 41.8 |  |  |  |  |
| 200-670 |  | 280.0 | 77.8 | 167.0 | 1480 | 450 | 80 | 3.1 |
|  |  | 793.0 | 220.3 | 150.0 |  |  |  |  |
|  |  | 935.0 | 259.7 | 140.0 |  |  |  |  |
|  | A | 270.0 | 75.0 | 144.0 |  | 355 | 78.5 |  |
|  |  | 729.7 | 202.7 | 127.0 |  |  |  |  |
|  |  | 900.0 | 250.0 | 115.0 |  |  |  |  |
|  | B | 260.0 | 72.2 | 124.0 |  | 315 | 77 |  |
|  |  | 669.8 | 186.0 | 107.0 |  |  |  |  |
|  |  | 864.4 | 240.0 | 93.0 |  |  |  |  |
|  | C | 250.0 | 69.4 | 10.0 |  | 250 | 76 |  |
|  |  | 637.4 | 177.0 | 88.0 |  |  |  |  |
|  |  | 770.0 | 213.9 | 80.0 |  |  |  |  |
| 250-400 |  | 400.0 | 111.1 | 50.0 | 1480 | 160 | 88 | 2.8 |
|  |  | 1052 | 292.2 | 39.0 |  |  |  |  |
|  |  | 1450 | 402.8 | 28.0 |  |  |  |  |
|  | A | 380.0 | 105.6 | 44.9 |  | 132 | 86 |  |
|  |  | 967.7 | 268.8 | 33.0 |  |  |  |  |
|  |  | 1310 | 363.9 | 24.0 |  |  |  |  |
|  | B | 379.0 | 105.3 | 38.0 |  | 110 | 83 |  |
|  |  | 915.3 | 254.3 | 27.0 |  |  |  |  |
|  |  | 1160 | 322.2 | 20.2 |  |  |  |  |
|  | C | 350.0 | 97.2 | 31.8 |  | 75 | 77.5 |  |
|  |  | 843.3 | 234.3 | 20.0 |  |  |  |  |
|  |  | 990.0 | 275.0 | 16.1 |  |  |  |  |
| 250-480 |  | 420.0 | 116.7 | 82.8 | 1480 | 280 | 87 | 3.3 |
|  |  | 1175 | 326.3 | 66.0 |  |  |  |  |
|  |  | 1608 | 447 | 50.0 |  |  |  |  |
|  | A | 400.0 | 111.1 | 69.0 |  | 220 | 85 |  |
|  |  | 1072 | 297.8 | 55.0 |  |  |  |  |
|  |  | 1450 | 402.8 | 41.6 |  |  |  |  |
|  | B | 370.0 | 102.8 | 58.0 |  | 200 | 83 |  |
|  |  | 975.2 | 270.9 | 45.5 |  |  |  |  |
|  |  | 1250 | 347.2 | 36.0 |  |  |  |  |
|  | C | 330.0 | 91.7 | 49.6 |  | 160 | 80 |  |
|  |  | 903.3 | 250.9 | 37.5 |  |  |  |  |
|  |  | 1090 | 302.8 | 31.2 |  |  |  |  |
| 250-600 |  | 800.0 | 222.2 | 131.0 | 1480 | 560 | 84 | 3.8 |
|  |  | 1243 | 245.3 | 116.0 |  |  |  |  |
|  |  | 1640 | 455.5 | 98.0 |  |  |  |  |
|  | A | 750.0 | 208.3 | 115.0 |  | 450 | 83.5 |  |
|  |  | 1154 | 320.6 | 100.0 |  |  |  |  |
|  |  | 1600 | 444.4 | 79.0 |  |  |  |  |
|  | B | 700.0 | 194.4 | 95.0 |  | 315 | 83 |  |
|  |  | 1051 | 292.0 | 83.0 |  |  |  |  |
|  |  | 1480 | 411.1 | 63.0 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 250-600 | C | 650.0 | 180.6 | 78.0 | 1480 | 250 | 82.5 | 3.8 |
|  |  | 970.0 | 269.4 | 66.0 |  |  |  |  |
|  |  | 1360 | 377.8 | 50.0 |  |  |  |  |
| 300-300 |  | 500.0 | 138.9 | 36.0 | 1480 | 110 | 86 | 4.6 |
|  |  | 1099 | 305.3 | 24.5 |  |  |  |  |
|  |  | 1475 | 409.7 | 17.0 |  |  |  |  |
|  | A | 480.0 | 133.3 | 31.8 |  | 90 | 84.5 |  |
|  |  | 1020 | 283.3 | 19.8 |  |  |  |  |
|  |  | 1425 | 395.8 | 12.1 |  |  |  |  |
|  | B | 460.0 | 127.8 | 26.5 |  | 75 | 82 |  |
|  |  | 970.0 | 269.4 | 15.5 |  |  |  |  |
|  |  | 1290 | 358.3 | 9.0 |  |  |  |  |
|  | C | 440.0 | 122.2 | 22.3 |  | 45 | 80 |  |
|  |  | 920.0 | 255.6 | 11.5 |  |  |  |  |
|  |  | 1170 | 325.0 | 7.5 |  |  |  |  |
| 300-435 |  | 700.0 | 194.4 | 67.5 | 1480 | 315 | 88 | 5.2 |
|  |  | 1679 | 466.3 | 53.0 |  |  |  |  |
|  |  | 2380 | 661.1 | 37.0 |  |  |  |  |
|  | A | 660.0 | 183.3 | 59.2 |  | 280 | 86.5 |  |
|  |  | 1577 | 438.0 | 45.0 |  |  |  |  |
|  |  | 2100 | 583.3 | 32.0 |  |  |  |  |
|  | B | 620.0 | 172.2 | 50.0 |  | 200 | 84 |  |
|  |  | 1476 | 410.0 | 36.5 |  |  |  |  |
|  |  | 1800 | 500.0 | 27.5 |  |  |  |  |
|  | C | 600.0 | 166.7 | 41.0 |  | 160 | 79 |  |
|  |  | 1361 | 378.0 | 27.5 |  |  |  |  |
|  |  | 1450 | 402.8 | 24.5 |  |  |  |  |
| 300-560 |  | 700.0 | 194.4 | 115.0 | 1480 | 630 | 86 | 4.2 |
|  |  | 1750 | 486.1 | 94.0 |  |  |  |  |
|  |  | 2350 | 652.8 | 76.0 |  |  |  |  |
|  | A | 680.0 | 188.9 | 92.0 |  | 450 | 85.5 |  |
|  |  | 1645 | 457.0 | 76.0 |  |  |  |  |
|  |  | 2170 | 602.8 | 61.5 |  |  |  |  |
|  | B | 650.0 | 180.6 | 77.5 |  | 355 | 85 |  |
|  |  | 1573 | 437.0 | 62.0 |  |  |  |  |
|  |  | 2130 | 591.7 | 47.0 |  |  |  |  |
|  | C | 620.0 | 172.2 | 65.0 |  | 280 | 83.5 |  |
|  |  | 1516 | 421.0 | 50.0 |  |  |  |  |
|  |  | 1980 | 550.0 | 37.5 |  |  |  |  |
| 300-700 |  | 900.0 | 250.0 | 183.0 | 1480 | 1120 | 85 | 3.5 |
|  |  | 1836 | 510.0 | 160.0 |  |  |  |  |
|  |  | 2100 | 583.3 | 150.6 |  |  |  |  |
|  | A | 960.0 | 266.7 | 160.0 |  | 900 | 84.6 |  |
|  |  | 1735 | 482.0 | 136.0 |  |  |  |  |
|  |  | 2030 | 563.9 | 126.0 |  |  |  |  |
|  | B | 800.0 | 222.2 | 135.0 |  | 630 | 84.3 |  |
|  |  | 1624 | 451.0 | 112.0 |  |  |  |  |
|  |  | 1880 | 522.2 | 104.0 |  |  |  |  |
|  | C | 700.0 | 194.4 | 110.5 |  | 560 | 84 |  |
|  |  | 1537 | 427.0 | 91.0 |  |  |  |  |
|  |  | 1600 | 444.4 | 77.0 |  |  |  |  |
| 350-360 |  | 600.0 | 166.7 | 45.5 | 1480 | 200 | 86.5 | 6.2 |
|  |  | 1733 | 481.4 | 32.0 |  |  |  |  |
|  |  | 2280 | 633.3 | 20.5 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 350-360 | A | 580.0 | 161.1 | 40.0 | 1480 | 160 | 85 | 6.2 |
|  |  | 1692 | 470.0 | 26.5 |  |  |  |  |
|  |  | 2160 | 600.0 | 17.0 |  |  |  |  |
|  | B | 560.0 | 155.5 | 34.0 |  | 132 | 83 |  |
|  |  | 1642 | 456.0 | 21.0 |  |  |  |  |
|  |  | 2080 | 577.8 | 12.8 |  |  |  |  |
|  | C | 540.0 | 150.0 | 27.9 |  | 110 | 80.5 |  |
|  |  | 1602 | 445.0 | 15.0 |  |  |  |  |
|  |  | 1900 | 527.8 | 9.0 |  |  |  |  |
| 350-430 |  | 1000 | 277.8 | 59.0 | 1480 | 450 | 87.5 | 8.5 |
|  |  | 2745 | 762.5 | 43.5 |  |  |  |  |
|  |  | 3500 | 972.2 | 31.0 |  |  |  |  |
|  | A | 950.0 | 263.9 | 50.5 |  | 355 | 85.5 |  |
|  |  | 2635 | 732.0 | 35.0 |  |  |  |  |
|  |  | 3450 | 958.3 | 22.0 |  |  |  |  |
|  | B | 900.0 | 250.0 | 43.0 |  | 280 | 84 |  |
|  |  | 2563 | 712.0 | 27.5 |  |  |  |  |
|  |  | 3250 | 902.8 | 18.5 |  |  |  |  |
|  | C | 890.0 | 247.2 | 36.0 |  | 220 | 81 |  |
|  |  | 2484 | 690.0 | 21.5 |  |  |  |  |
|  |  | 3200 | 888.9 | 13.0 |  |  |  |  |
| 350-510 |  | 1350 | 375.0 | 94.0 | 1480 | 630 | 88.5 | 6.7 |
|  |  | 2610 | 725.0 | 70.0 |  |  |  |  |
|  |  | 3700 | 1028 | 48.3 |  |  |  |  |
|  | A | 1100 | 305.6 | 82.0 |  | 560 | 87 |  |
|  |  | 2430 | 6750 | 60.0 |  |  |  |  |
|  |  | 3500 | 972.2 | 42.0 |  |  |  |  |
|  | B | 750.0 | 208.3 | 73.0 |  | 400 | 86 |  |
|  |  | 2232 | 620.0 | 50.0 |  |  |  |  |
|  |  | 2850 | 791.7 | 37.0 |  |  |  |  |
|  | C | 505 | 140.3 | 61 |  | 315 | 79 |  |
|  |  | 2070 | 575 | 38 |  |  |  |  |
|  |  | 2350 | 652.8 | 33.2 |  |  |  |  |
| 350-630 |  | 1470 | 408.3 | 138.5 | 1480 | 1000 | 85 | 6.9 |
|  |  | 2160 | 600 | 126.2 |  |  |  |  |
|  |  | 2800 | 777.8 | 107 |  |  |  |  |
|  | A | 1290 | 358.3 | 128 |  | 900 | 84 |  |
|  |  | 2000 | 556 | 116 |  |  |  |  |
|  |  | 2600 | 722 | 98.3 |  |  |  |  |
|  | B | 1185 | 329.2 | 117.8 |  | 800 | 82 |  |
|  |  | 1920 | 533.3 | 106 |  |  |  |  |
|  |  | 2500 | 697.4 | 88.5 |  |  |  |  |
|  | C | 1110 | 308.3 | 107.8 |  | 710 | 80 |  |
|  |  | 1830 | 508.3 | 95.6 |  |  |  |  |
|  |  | 2380 | 661 | 78 |  |  |  |  |
|  | D | 1050 | 291.7 | 93.8 |  | 560 | 78 |  |
|  |  | 1695 | 470.8 | 83 |  |  |  |  |
|  |  | 2200 | 611 | 68 |  |  |  |  |
| 400-560 |  | 1535 | 426.3 | 98 | 1480 | 800 | 85 | 7 |
|  |  | 2635 | 731.9 | 86 |  |  |  |  |
|  |  | 3420 | 950 | 70.8 |  |  |  |  |
|  | A | 1470 | 408.3 | 91 |  | 710 | 83 |  |
|  |  | 2520 | 700 | 79 |  |  |  |  |
|  |  | 3270 | 908.3 | 63.9 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 400-560 | B | 1420 | 394 | 82.6 | 1480 | 630 | 81 | 7 |
|  |  | 2418 | 671.6 | 71.8 |  |  |  |  |
|  |  | 3140 | 872 | 56.8 |  |  |  |  |
|  | C | 1400 | 388.9 | 76 |  | 630 | 79 |  |
|  |  | 2312 | 642 | 64 |  |  |  |  |
|  |  | 3015 | 837.5 | 49 |  |  |  |  |
|  | D | 1380 | 383.3 | 69 |  | 5600 | 77 |  |
|  |  | 2236 | 621 | 57.8 |  |  |  |  |
|  |  | 2900 | 805.6 | 43.8 |  |  |  |  |
| 400-600 |  | 1919 | 533 | 129.7 | 1480 | 1250 | 86 | 7.5 |
|  |  | 3177 | 882.4 | 113 |  |  |  |  |
|  |  | 4100 | 1139 | 93.6 |  |  |  |  |
|  | A | 1780 | 494.4 | 119 |  | 1120 | 84 |  |
|  |  | 3007 | 835.3 | 103.6 |  |  |  |  |
|  |  | 3910 | 1086 | 83.6 |  |  |  |  |
|  | B | 1740 | 483.3 | 109.2 |  | 1000 | 82 |  |
|  |  | 2922 | 811.8 | 93 |  |  |  |  |
|  |  | 3800 | 1056 | 70.8 |  |  |  |  |
|  | C | 1600 | 444.4 | 99.8 |  | 900 | 80 |  |
|  |  | 2732 | 758.8 | 83.7 |  |  |  |  |
|  |  | 3550 | 986 | 63 |  |  |  |  |
|  | D | 1530 | 425 | 90 |  | 800 | 78 |  |
|  |  | 2642 | 706 | 74 |  |  |  |  |
|  |  | 3380 | 938.9 | 57 |  |  |  |  |
| 500-520 |  | 1900 | 527.8 | 33.2 | 980 | 280 | 87 | 4.8 |
|  |  | 3218 | 893.8 | 25 |  |  |  |  |
|  |  | 3960 | 1100 | 17.7 |  |  |  |  |
|  | A | 1830 | 508.3 | 30.5 |  | 250 | 86 |  |
|  |  | 3088 | 857.8 | 23 |  |  |  |  |
|  |  | 3800 | 1056 | 16.3 |  |  |  |  |
|  | B | 1750 | 486 | 28.6 |  | 220 | 84 |  |
|  |  | 2965 | 823.3 | 21 |  |  |  |  |
|  |  | 3650 | 1014 | 15.3 |  |  |  |  |
|  | C | 1680 | 466.7 | 26 |  | 200 | 82 |  |
|  |  | 284 | 790.65 | 18.4 |  |  |  |  |
|  |  | 3485 | 968 | 13 |  |  |  |  |
|  | D | 1600 | 444.4 | 23.8 |  | 180 | 80 |  |
|  |  | 2732 | 758.9 | 16.3 |  |  |  |  |
|  |  | 3180 | 883.3 | 11.75 |  |  |  |  |
| 500-650 |  | 1850 | 513.9 | 52.5 | 980 | 500 | 88.5 | 5.7 |
|  |  | 3510 | 975 | 41.5 |  |  |  |  |
|  |  | 4500 | 1250 | 31 |  |  |  |  |
|  | A | 1800 | 500 | 49.8 |  | 450 | 86 |  |
|  |  | 3353 | 931 | 38.7 |  |  |  |  |
|  |  | 4230 | 1175 | 28.5 |  |  |  |  |
|  | B | 1740 | 483.3 | 46.4 |  | 400 | 84 |  |
|  |  | 3173 | 881 | 36 |  |  |  |  |
|  |  | 4000 | 1112 | 26.5 |  |  |  |  |
|  | C | 1660 | 461.1 | 42.2 |  | 355 | 82 |  |
|  |  | 3015 | 837.5 | 33.2 |  |  |  |  |
|  |  | 3830 | 1064 | 25 |  |  |  |  |
|  | D | 1560 | 433.3 | 37.6 |  | 315 | 80 |  |
|  |  | 2768 | 768.8 | 29.7 |  |  |  |  |
|  |  | 3600 | 1000 | 21.8 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 500-710 |  | 2300 | 638.9 | 73.1 | 980 | 900 | 88.5 | 5.8 |
|  |  | 3852 | 1070 | 64.4 |  |  |  |  |
|  |  | 5040 | 1400 | 54 |  |  |  |  |
|  | A | 2200 | 611.1 | 67.2 |  | 800 | 87 |  |
|  |  | 3672 | 1020 | 59.2 |  |  |  |  |
|  |  | 4840 | 1344 | 47.1 |  |  |  |  |
|  | B | 2100 | 583.3 | 60.3 |  | 710 | 85 |  |
|  |  | 3470 | 964 | 53 |  |  |  |  |
|  |  | 4320 | 1200 | 43 |  |  |  |  |
|  | C | 200 | 555.6 | 56.4 |  | 560 | 83 |  |
|  |  | 3204 | 890 | 47.7 |  |  |  |  |
|  |  | 3960 | 1100 | 39 |  |  |  |  |
|  | D | 1920 | 533.3 | 50 |  | 500 | 81 |  |
|  |  | 3024 | 840 | 42 |  |  |  |  |
|  |  | 3550 | 986.1 | 34.2 |  |  |  |  |
| 500-800 |  | 2590 | 719.4 | 88.7 | 980 | 1120 | 89 | 6.9 |
|  |  | 3996 | 1110 | 80.6 |  |  |  |  |
|  |  | 5190 | 1442 | 67.9 |  |  |  |  |
|  | A | 2460 | 683.3 | 78.4 |  | 900 | 87 |  |
|  |  | 3600 | 1000 | 72.8 |  |  |  |  |
|  |  | 4680 | 1300 | 61.8 |  |  |  |  |
|  | B | 2340 | 650 | 69.8 |  | 800 | 85 |  |
|  |  | 3204 | 890 | 65.3 |  |  |  |  |
|  |  | 4100 | 1139 | 57 |  |  |  |  |
|  | C | 2200 | 611.1 | 61 |  | 630 | 83 |  |
|  |  | 2880 | 800 | 58 |  |  |  |  |
|  |  | 3600 | 1000 | 52 |  |  |  |  |
| 500-860 |  | 2520 | 700 | 124 | 980 | 1600 | 89 | 6.9 |
|  |  | 4183 | 1162 | 111.2 |  |  |  |  |
|  |  | 5440 | 1511 | 96.2 |  |  |  |  |
|  | A | 2380 | 661.1 | 112.4 |  | 1400 | 87 |  |
|  |  | 3996 | 1110 | 100.7 |  |  |  |  |
|  |  | 5140 | 1428 | 86 |  |  |  |  |
|  | B | 2250 | 625 | 102.4 |  | 1250 | 83 |  |
|  |  | 3780 | 1050 | 90.4 |  |  |  |  |
|  |  | 4870 | 1353 | 77.5 |  |  |  |  |
|  | C | 2115 | 587.35 | 90.4 |  | 1120 | 80 |  |
|  |  | 3528 | 980 | 80.4 |  |  |  |  |
|  |  | 4320 | 1300 | 70.6 |  |  |  |  |
| 600-560 |  | 3140 | 872.2 | 31.9 | 980 | 400 | 87 | 6 |
|  |  | 4716 | 1310 | 24.2 |  |  |  |  |
|  |  | 6100 | 1694 | 14.3 |  |  |  |  |
|  | A | 2970 | 825 | 28.5 |  | 355 | 85 |  |
|  |  | 4428 | 1230 | 21.5 |  |  |  |  |
|  |  | 5670 | 1575 | 13.1 |  |  |  |  |
|  | B | 2790 | 775 | 23.8 |  | 250 | 83 |  |
|  |  | 4046 | 1124 | 17.8 |  |  |  |  |
|  |  | 5054 | 1459.7 | 11 |  |  |  |  |
|  | C | 2620 | 727.8 | 20.2 |  | 220 | 81 |  |
|  |  | 3787 | 1052 | 15.4 |  |  |  |  |
|  |  | 4860 | 1350 | 10 |  |  |  |  |
| 600-630 |  | 3170 | 880.6 | 47 | 980 | 630 | 88 | 7.8 |
|  |  | 4737 | 1316 | 39 |  |  |  |  |
|  |  | 5940 | 1650 | 30 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 600-630 | A | 2980 | 827.8 | 40.8 | 980 | 560 | 86 | 7.8 |
|  |  | 4420 | 1230 | 34.1 |  |  |  |  |
|  |  | 5580 | 1550 | 26 |  |  |  |  |
|  | B | 2800 | 777.8 | 34.6 |  | 450 | 84 |  |
|  |  | 4080 | 1133 | 29.1 |  |  |  |  |
|  |  | 5040 | 1400 | 23.2 |  |  |  |  |
|  | C | 2630 | 730.6 | 29 |  | 355 | 80 |  |
|  |  | 3755 | 1043 | 24.8 |  |  |  |  |
|  |  | 4450 | 1236 | 20.2 |  |  |  |  |
| 600-710 |  | 2915 | 809.7 | 68.8 | 980 | 900 | 89 | 6.5 |
|  |  | 4630 | 1286 | 58.4 |  |  |  |  |
|  |  | 6050 | 1680 | 43.4 |  |  |  |  |
|  | A | 2740 | 761 | 60 |  | 800 | 87 |  |
|  |  | 4320 | 1200 | 50 |  |  |  |  |
|  |  | 5680 | 1578 | 36 |  |  |  |  |
|  | B | 2595 | 721 | 60 |  | 630 | 85 |  |
|  |  | 4050 | 1125 | 50 |  |  |  |  |
|  |  | 5220 | 1450 | 36 |  |  |  |  |
|  | C | 2425 | 673.6 | 43.8 |  | 500 | 83 |  |
|  |  | 3752 | 1042 | 35.2 |  |  |  |  |
|  |  | 4680 | 1300 | 26.8 |  |  |  |  |
| 600-860 |  | 3750 | 763.9 | 102 | 980 | 1600 | 89 | 8.5 |
|  |  | 5538 | 1538 | 87.5 |  |  |  |  |
|  |  | 6910 | 1919 | 70 |  |  |  |  |
|  | A | 3525 | 949.2 | 91 |  | 1400 | 87 |  |
|  |  | 5109 | 1419 | 77 |  |  |  |  |
|  |  | 6490 | 1803 | 58 |  |  |  |  |
|  | B | 3300 | 916.7 | 78 |  | 1120 | 85 |  |
|  |  | 4680 | 1300 | 65.5 |  |  |  |  |
|  |  | 5750 | 1597 | 53 |  |  |  |  |
|  | C | 3000 | 833.3 | 65 |  | 900 | 83 |  |
|  |  | 4355 | 1209 | 56 |  |  |  |  |
|  |  | 5050 | 1403 | 46 |  |  |  |  |
| 700-600 |  | 4265 | 1185 | 37.8 | 980 | 710 | 87 | 8.2 |
|  |  | 6568 | 1824 | 29.8 |  |  |  |  |
|  |  | 8100 | 2250 | 22.6 |  |  |  |  |
|  | A | 4180 | 1161 | 34.4 |  | 630 | 85 |  |
|  |  | 6322 | 1756 | 27.8 |  |  |  |  |
|  |  | 7840 | 2178 | 21.2 |  |  |  |  |
|  | B | 3970 | 1103 | 31.3 |  | 560 | 83 |  |
|  |  | 6048 | 1680 | 25.9 |  |  |  |  |
|  |  | 7450 | 2069 | 20.9 |  |  |  |  |
|  | C | 3770 | 1047 | 28.8 |  | 500 | 81 |  |
|  |  | 5895 | 1638 | 24 |  |  |  |  |
|  |  | 7000 | 1944 | 20 |  |  |  |  |
| 700-710 |  | 3650 | 1014 | 58.5 | 980 | 1000 | 87 | 8 |
|  |  | 6516 | 1810 | 43.5 |  |  |  |  |
|  |  | 8470 | 2353 | 28.2 |  |  |  |  |
|  | A | 3500 | 972.2 | 54.5 |  | 900 | 85 |  |
|  |  | 6278 | 1744 | 40.2 |  |  |  |  |
|  |  | 8050 | 2236 | 26.2 |  |  |  |  |
|  | B | 3360 | 933.3 | 50.4 |  | 800 | 83 |  |
|  |  | 5971 | 1659 | 36.8 |  |  |  |  |
|  |  | 7560 | 2100 | 25.2 |  |  |  |  |
| 泵型号（Type） |  | 流量（Capacity） |  | 扬程 Head (m) | 转速 Speed (r/min) | 电机功率 Motor Power (kw) | 效率 Eff (%) | 必须汽蚀余量 (NPSH)r (m) |
|  |  | (m3/h) | (L/s) |  |  |  |  |  |
| 700-710 | C | 3225 | 895.8 | 45 | 980 | 710 | 81 | 8 |
|  |  | 5742 | 1595 | 31.8 |  |  |  |  |
|  |  | 7130 | 1981 | 22.8 |  |  |  |  |
| 700-800 |  | 4680 | 1300 | 93 | 980 | 2000 | 89 | 8.8 |
|  |  | 7416 | 2060 | 79.6 |  |  |  |  |
|  |  | 9850 | 2736 | 58 |  |  |  |  |
|  | A | 4425 | 1229 | 81.8 |  | 1600 | 87 |  |
|  |  | 6959 | 1933 | 67.8 |  |  |  |  |
|  |  | 9180 | 2550 | 48 |  |  |  |  |
|  | B | 4200 | 1167 | 70.8 |  | 1400 | 85 |  |
|  |  | 6552 | 1820 | 58 |  |  |  |  |
|  |  | 8420 | 2339 | 42.8 |  |  |  |  |
|  | C | 3950 | 1097 | 59 |  | 1000 | 83 |  |
|  |  | 6012 | 1670 | 47.5 |  |  |  |  |
|  |  | 7520 | 2086 | 36 |  |  |  |  |
| 800-800 |  | 5870 | 1631 | 36.6 | 730 | 800 | 87 | 7 |
|  |  | 9090 | 2525 | 26.8 |  |  |  |  |
|  |  | 11000 | 3056 | 18.2 |  |  |  |  |
|  | A | 5575 | 1509 | 33.6 |  | 710 | 85 |  |
|  |  | 8622 | 2395 | 24.3 |  |  |  |  |
|  |  | 10370 | 2881 | 16.3 |  |  |  |  |
|  | B | 5295 | 1471 | 30.9 |  | 710 | 83 |  |
|  |  | 8280 | 2300 | 22.3 |  |  |  |  |
|  |  | 9850 | 2736 | 14.8 |  |  |  |  |
|  | C | 5030 | 1397 | 28.2 |  | 560 | 81 |  |
|  |  | 7860 | 2183 | 19.8 |  |  |  |  |
|  |  | 9290 | 2581 | 13.5 |  |  |  |  |
| 800-900 |  | 6375 | 1771 | 53.8 | 730 | 1400 | 88 | 6.3 |
|  |  | 9023 | 2506 | 45.8 |  |  |  |  |
|  |  | 11620 | 3228 | 34.6 |  |  |  |  |
|  | A | 6120 | 1700 | 50 |  | 1250 | 86 |  |
|  |  | 8658 | 2405 | 42.2 |  |  |  |  |
|  |  | 11160 | 3100 | 32.2 |  |  |  |  |
|  | B | 5815 | 1615 | 45.4 |  | 1120 | 84 |  |
|  |  | 8262 | 2295 | 38.5 |  |  |  |  |
|  |  | 10600 | 2944 | 29.6 |  |  |  |  |
|  | C | 5550 | 1542 | 41.5 |  | 1000 | 80 |  |
|  |  | 7884 | 2190 | 35.4 |  |  |  |  |
|  |  | 10120 | 2811 | 27 |  |  |  |  |
|  | D | 5270 | 1464 | 37 |  | 900 | 80 |  |
|  |  | 7452 | 2070 | 32.2 |  |  |  |  |
|  |  | 9620 | 2672 | 24.5 |  |  |  |  |
| 800-990 |  | 6600 | 1833 | 73.8 | 730 | 2000 | 89 | 6.7 |
|  |  | 9810 | 2725 | 62.5 |  |  |  |  |
|  |  | 11660 | 3239 | 51.2 |  |  |  |  |
|  | A | 6335 | 1757 | 66 |  | 1800 | 87 |  |
|  |  | 9300 | 2583 | 55.3 |  |  |  |  |
|  |  | 11090 | 3081 | 45.3 |  |  |  |  |
|  | B | 6080 | 1689 | 59.5 |  | 1600 | 85 |  |
|  |  | 8892 | 2470 | 49.4 |  |  |  |  |
|  |  | 10400 | 2889 | 41.2 |  |  |  |  |
|  | C | 5770 | 1603 | 53.8 |  | 1400 | 83 |  |
|  |  | 8525 | 2368 | 44.3 |  |  |  |  |
|  |  | 9685 | 2690 | 38.8 |  |  |  |  |

安装使用说明

一、特别提示：

泵的安装须由经过培训的，对水泵安装富有经验的人员进行。

二、一般要求：

（一）泵与电机联轴器的轴向和径向偏差不超过0.04mm，每次在联轴器的两端均匀旋转量具90°，用游标卡尺或千分尺检查，所有点的读数必须均匀。

（二）不允许将泵作为管路的支点，管路在靠近泵的地方应设可靠支撑，泵与管路连接处不允许传递任何应力和变形。管路的公称直径必须大于或等于相应泵的口径，必须用适当的方法补偿的热路膨胀，使泵不受额外的负载。

1、泵的安装和调整

泵的安装须由经过培训的，对水泵安装富有经验的人员进行。

安装形式：

1、测量并记下泵的位置。

2、把泵电机机组放在基础上，地脚螺栓插入基础中并调整。基础和底座之间保留4-5mm间隙。

3、对基础螺栓灌浆并让其坚固。

4、基础坚固后均匀地拧紧地脚螺栓。

5、调整并对底座灌浆。

2、轴承润滑

轴承在制造厂已加油脂、起动前检查轴承，如果在运输和储存中有杂质进入轴承或油脂已凝结固化或油脂已泄漏，起动前必须更换油脂。

轴承至多运行两年后必须更换油脂。每次更换油脂必须拆除轴承。更换油脂前用汽油或类似的介质清洗轴承、轴承体和轴承压盖，并擦干净。在球轴承和滚珠轴承中完全填料油脂，而在轴承压盖中只填充一半油脂。用油枪在轴承体上部的油嘴中加油。

滑动轴承用介质或外接水源润滑，为防止轴承堵塞，每运行8000小时或至多两年后，必须清洁轴承，并确保润滑管路畅通。

### OPERATION AND MAINTENANCE INSTRUCTION MANUAL

● Caution: Installation of pumps must be expert and correlative train.

● General Require:

(Ⅰ) Axial and Radial clearance of pump and motor coupling less than 0.04mm. Use of the vernier caliper or micrometer inspect both the end of coupling that equal rotate instrument 90º,every point read data must be equally.

(Ⅱ) Pump shall not be pivot of pipeline and pipeline must be set of fit support against pump. The joint of pump and pipeline can’t transmit any stress and distortion. nominal diameter of pipeline must be excess or equal diameter of pump, and drop suitable method for heat expansion of equalize pipe and loading of superfluity.

- Installation and adjustment of pump

Caution: Installation of pumps must be expert and correlative train.

#### Installation Type

- Measure and writing position of pump

- Pump unites put on base floor, anchor bolts insert base floor and adjustment. Remain 4~5mm between base floor and bedplate.

- Grouting base bolts and fitting.

- After base tightness, equally screw anchor bolts.

- Adjust and Grouting the bedplate.

- Bearing lubrication

Bearing already fill oil in manufacture and before start-up check bearing. If bearing or oil grease already freeze or leaking in transmit or store. Please alter oil before start-up.

Bearing must be change oil grease after operation two years. Each time change oil grease must disassembly bearing. Before change oil grease, use of gasoline or similar medium clear bearing. Bearing body and bearing gland, fill over oil grease the ball bearing, but the bearing gland just fill half capacity. Use of the oil gun fill the top of bearing body in nozzle. Slip bearing use of medium or connect external water for protect bearing block. After operation 8000 hours or more two years, must be clear bearing for lubrication pipeline expedite。

3、轴封的维护

如果轴封大量泄漏或长时间停机，泵启运前要安装或更换填料。泵运行时填料函处有少量滴水，填料压得太紧会使轴套发热并磨损，因此填料必须轻轻地、均匀地压紧。

机械密封：机械密封无需特别维护，每天检查它是否发热。如果机械密封明显泄漏，拆开并检查，必要的话更换机械密封。

4、拆卸

只要拆开泵盖，不必拆卸进出水管路，就能拆除整个转子部件；

- 关闭进出口泵盖，打开放水螺塞和放气螺塞，将水和气排出；

- 松开泵联轴器与电机联轴器之间的紧固件；

- 松开并压出填料盖；

- 松开泵盖与泵体之间的连接螺栓，拿掉泵盖；

- 松开轴承体和泵体之间的连接螺栓，拆下转子部件；

- 拆下泵联轴器和轴承压盖；

- 松开螺母，从轴上压出轴承体、轴承体包括轴承，确保压力均匀，不要用榔头，否则会损坏轴承；

- 拆下填料、填料环和衬套，松开轴螺母，拆下轴套。叶轮和轴之间是间隙配合，所以叶轮能比较容易地拆下。如果拆不下，用木榔头敲打轮毂。

5、重新装配

重新装配可按上述拆卸顺序的相反方向进行。装配和拆卸油封、轴承和泵体、叶轮密封环时要按照规范的装配工艺或安装使用说明。

在装泵盖前为防止填料环进入填料箱，把填料环粘在填料压盖上。

确保泵和电机联轴器与泵和电机的轴端齐平，轴不能突出。

6、运行/起动/停止

准备

泵的灌注和辅助管路检查

泵在起动前必须很好地放气并用介质灌注，进口管路中的截止阀必须适当打开。

注意：泵不允许干运行！安全打开辅助管路（冲洗、密封、冷却液等），并检查流量。

检查轴承润滑剂和轴封

检查转子转向

电机转向应与泵壳上的箭头方向相同，在连接电机前检查泵的转向。

- Main of shaft seal

If shaft seal lot of leaking or long time shut-off, so that installation equipment or change packing. Stuff box have little drop water when operation. If packing pressures more tie that shaft sleeve heat and wearing. Packing must be given gently and equally pressure machine seal. Machine seal needn’t special maintain but whether every day shall be overheat. If machine seal have observe leaking, disassembly and check , if necessary, change machine seal.

4. Disassembly

Just disassembly pump cover, don’t disassembly inlet and outlet pipework, it’s disassembly whole rotating parts.

- Shut-off inlet and outlet pump cover, then open drain water screw plug. And drain water and gas.

- Loosen fitting parts between pump coupling and motor coupling.

- Loosen and extrude packing cover.

- Loosen joint bolts between pump cover and pump body then remove pump cover.

- Loosen joint bolts between bearing body and pump body then disassembly rotating parts.

- Disassembly pump coupling and bearing gland.

- Loosen nut, pressure bearing body from shaft. The bearing body including bearing, comfier pressure equally. Don’t use of hammer whether damage bearing.

- Disassembly packing, packing ring and gas    then loosen shaft nut, disassembly shaft sleeve.

It’s clearance assort between Impeller and shaft so that impeller easily disassembly. If not, use of wood hammer beat impeller hub.

5. Renew assembly

Renew assembly according to counter disassembly circulate. It’s according to installation and assembly workmanship assembly and disassembly oil seal. Bearing and pump body, impeller seal ring.

Before assembly pump cover in order to prevent packing ring enter stuff box so that packing ring coherent packing gland.

Confirm pump, motor and shaft end of pump and motor together, shaft not extrude.

6. Operation /start-up/shut-off

#### Prepare

Filling of pump and Aux. Pipeline inspection

Before start-up, the pump must be perfect drain gas and fill medium and check valve of inlet pipeline must be suitable open.

Note: Pump can’t empty operation safely open Aux pipeline (flush, seal, cooling liquid etc.) and check capacity.

Check bearing lubrication and shaft seal

Check rotating direction.

Motor direction must be same direction with arrowhead of pump casing. Before connect motor, inspect direction of pump.

起动

－如果没有止回阀就关闭出口阀；

－安全打开进口阀（如果有的话）；

－如果有的话，打开轴封和轴承的外接水源阀门；

－泵一开始泵水、压力表压力就上升，慢慢打开出口阀，使泵在规定的参数范围内工作。

泵只有在起动和停止的时候关闭出口阀，否则泵将发热或损坏。

－关闭出口管路中的截止阀；

－如果出口管路中有止回阀，则截止阀可以维持打开状态以得到一个回压；

－关闭电机；

－关闭辅助管路；

－如果有冷却水的话，等泵冷却后再关闭。

－如果发生霜冻或长时间停车，排空水泵和冷却腔（如果有的话），或者采取其它防冻措施。如果泵配的是填料密封，拆除填料。如果泵处理的是污水，为防止在停车期间被腐蚀，排安并冲洗。

7、维护/运行管理

泵运行时应保持平稳，否则轴承和轴封将会损坏，泵不允许干运行。泵不能长时间在出口阀关闭的情况下运行。轴承最高温度允许超出环境温度50℃，或不超过90℃。

在泵运行时，辅助管路中的阀门必须保持打开。如果泵配的是填料密封，运行时应有少量滴水，填料压盖应轻轻地压紧。

定期检查备用泵，确保泵能正常运行，定期转动泵轴。定期检查联轴器部件，一经发现磨损即行更换。外接密封、冷却和润滑水必须高出进口压力1.2～2.0bar。

#### Start-up

If haven’t check valve that close outlet valve.

Open inlet valve (if exist)

If exist, open shaft seal and external connect water valve of bearing.

Open the power resource.

Pump start-up suction water so that pressure of pressure gage rise. Then slowly open outlet valve for pump working in normal parameter rang.

Pump close outlet valve only just start-up and shut off, whether pump shall be overheat or damage.

#### Shut-off

Close check valve of outlet pipework.

If outlet pipework have check valve, so that check valve can remain open state for a return pressure.

Close motor

If exist，close inlet valve.

Close Aux. Pipework

If cooling water exist，after pump cooling then close.

If occur frost or long time stop operation that drain pump and cooling house(if exist) or adopt another method for protect frost. If pump is packing seal that disassembly packing. If pump deal with sewage that drain empty and flush for prevent corrupt when stop operation period.

7. Maintain/operation management

Pump remain placidity in operation otherwise bearing and shaft seal shall be damage and pump don’t empty operation in outlet close consider. Max temperature of bearing allow to excess ambient temperature 50℃ or less than 90℃.

Valve of Aux. Pipework must be remaining open in operation. If pump drop packing seal that have litter drop water and packing gland shall be gently tie.

Regular inspect stand pump and rotating pump shaft for pump normal operation. Regular inspect coupling parts, seek wear as soon as alter pressure of external connect seal, cooling and lubrication must high than inlet pressure 1.2~2.0 bar.

8、可能发生的故障及其解决方法

| 1、泵不出水，压力表及真空表指针剧烈跳动 | 注入泵的水不够，进水管漏气。 | 再往泵内注水，堵塞漏气处。 |
| --- | --- | --- |
| 2、泵不吸水。但真空表表示高度真空 | 底阀没有全开或淤塞，吸水管阻力太大，吸水高度太高。 | 较平或更换底阀，清洗或更换吸水管，降低吸水高度。 |
| 3、泵不出水，出水处压力表显示有压力。 | 泵轴旋转方向不对，出水管阻力太大，叶轮淤塞，转速不够。 | 改正转向，检查水管长度或淤塞，清洗叶轮，增加转速。 |
| 4、泵流量减少或扬程下降。 | 叶轮或进口管路阻塞，密封环或叶轮磨损严重，转速低于规定值。 | 清洗叶轮或管路，更换损坏的零件，调整到额定转速。 |
| 5、泵消耗的功率过大。 | 填料压得太紧，叶轮与双吸密封环磨损，流量过大。 | 拧松填料压盖，消除机械摩擦关小出水闸阀。 |
| 6、泵内声音反常，吸不上水。 | 吸水阻力大，吸水高度过高，吸水管漏气，流量过大，发生汽蚀。 | 查水管及底阀，减少吸水高度，堵塞漏气处，调节出水闸阀在规定工况内 |
| 7、泵振动厉害。 | 泵发生汽蚀，叶轮不平衡，泵轴与电机不同心，地脚螺栓松动。 | 消除汽蚀，叶轮较平衡，较泵轴和电机轴的同轴度，拧紧地脚螺栓。 |
| 8、轴承过热。 | 润滑油不足或过多，或变质，泵轴与电机轴不同心。 | 检查油量，清洗轴承并换油，校正泵轴与电机轴的同轴度 |

8、Possible trouble and remedies

| Troubles | Causes | Remedies |
| --- | --- | --- |
| 1. Water delivery failure, the arrows of the pressure gaage and vacuum gate making fierce vibration | Insufficient poured liquid before operation, air leakage from the pipe and instrument | Pour water into the pump, tighten or seal the leaking |
| 2. Water delivery failure, vacuum gage displaying high vacuum | Foot valve closed or blocked, suction pipe having large resistance fore and suction water height | Adjust or replace bottom valve, or replace suction pipe, low the suction water height |
| 3. Pressure gage on the outlet displaying pressure, but water delivery failure | Large resistance force for outlet pipe, wrong rotation direction, impeller blocked, rotating speed too low | Check or shorten water pipe, test rotation direction of motor, increase rotating speed. |
| 4. Low capacity | Pump blocked, wearing ring haaving too much, fricttion, insufficient rotaating speed | Clean pump and pipe, replace wearing ring,increase rotating speed |
| 5. Pump consuming too much power | Too tight gland, packing house heating, impeller damaged, supplying water increasing | Loose gland, replace the impeller, close the brake valve a little to low capacity |
| 6. Abnormal noise, sucting water failure | Open the valve too much, resistance inside the suction pipe too large, the suction height too great, air into the suction, the liquid temperature too high | Close the brake valve a little to low capacity, check suction pipe and foot valve, low suction height, tighten or block air leakage, low liquid temperature. |
| 7. Vibration | Eccentric alignment of the pump shaft and motor shaft | Adjust the concentricity of the whole unit |
| 8. Brearing overheat | Lubrication oil poor, eccent- ric alignment of the pump shaft and motor shaft oil ring not rotating | Heat, adjust the concentrici- ty of the whole unit, check or clean bearing body. |

成套供应范围

Supply Range of Complete Set

1、泵

2、原动机，根据用户需要，可配带防爆电机，普通电机，汽轮机或柴油机

3、底座和地脚螺栓（根据需要）

4、联轴器和联轴器罩

5、带部分冷却和密封管路系统或辅件，不供辅助泵

1. Pump

2. Motor, anti-explosion and general motor, turbine or diesel can be supplied according to the customer’s requirements.

3. Base and anchor bolts.(according requirement)

4. Coupling and coupling cap.

5. Parts of cooling and sealing pipe system or accessories, auxiliary pump is not supplied.

订货须知

### Ordering Instructions

1、应按照使用条件的规格、材料、冷却和密封管路系统及原动机。在订货时应提供流量、扬程、吸入压力、密度、温度及介质等，并指出介质的易燃性、易爆性、毒性、腐蚀性、结晶性以及是否允许封液渗入介质内。

2、若对原动机有特殊要求时，用户应说明现场条件，环境温度和湿度，安装地点及类别（防爆、防火等要求）电压大小。

3、若用户需要选用轴封，在订货时由制造厂按使用条件决定供货的型号及规格、材料，也可按用户要求的供货。

4、以上要求均填写出在《数据单》上。

1. Pump’s size, material, cooling and sealing piping system and motor should be decided according to used conditions. When ordering the following condition should be given: capacity. head, suction pressure, such as inflammable, explosive, toxic, corrosiveness, crystalline and whether sealing liquid is allowed to enter into pump medium.

2. If special motor is required. The customer should specify site conditions, ambient temperature and moisture, installation place and type(anti-explosive and anti-fire ect.). voltage.

3. If the customer selects shaft sleeve. The type, size and material of shaft sleeve will be decided by manufacturer according to use condition and also according to customer’s requirement.

- The above requirements should be written on data sheet.